## Sheet1
WND WattNode Modbus Register List
Firmware Versions: 33 and 1033 |  |  |  | Date: 2019-04-08
Products: WND-WR-MB, WND-M1-MB, WND-M0-MB
Note: You may use any desired names for the registers, since only the register numbers are used by the protocol.
Note: The register numbers are not entirely in consecutive order.
Measurement Register List - Floating-Point
| Registers | Name | WNC Name | Units | Access | Default | Description
Energy Registers
| 1001, 1002 | EnergySum | EnergySum | kWh | Read/Write |  | Total net (bidirectional) energy
| 1005, 1006 | EnergySumNR | EnergySumNR | kWh | Read-Only |  | Total net (bidirectional) energy - non resettable
| 1101, 1102 | Energy1 | EnergyA | kWh | Read/Write |  | Net (bidirectional) energy, meter element 1
| 1103, 1104 | Eneryg2 | EnerygB | kWh | Read/Write |  | Net (bidirectional) energy, meter element 2
| 1105, 1106 | Energy3 | EnergyC | kWh | Read/Write |  | Net (bidirectional) energy, meter element 3
| 1003, 1004 | EnergyPosSum | EnergyPosSum | kWh | Read/Write |  | Total positive energy
| 1007, 1008 | EnergyPosSumNR | EnergyPosSumNR | kWh | Read-Only |  | Total positive energy - non resettable
| 1107, 1108 | EnergyPos1 | EnergyPosA | kWh | Read/Write |  | Positive energy, meter element 1
| 1109, 1110 | EnergyPos2 | EnergyPosB | kWh | Read/Write |  | Positive energy, meter element 2
| 1111, 1112 | EnergyPos3 | EnergyPosC | kWh | Read/Write |  | Positive energy, meter element 3
| 1113, 1114 | EnergyNegSum | EnergyNegSum | kWh | Read/Write |  | Negative energy, sum of active phases
| 1115, 1116 | EnergyNegSumNR | EnergyNegSumNR | kWh | Read-Only |  | Negative energy, sum of active phases - non resettable
| 1117, 1118 | EnergyNeg1 | EnergyNegA | kWh | Read/Write |  | Negative energy, meter element 1
| 1119, 1120 | EnergyNeg2 | EnergyNegB | kWh | Read/Write |  | Negative energy, meter element 2
| 1121, 1122 | EnergyNeg3 | EnergyNegC | kWh | Read/Write |  | Negative energy, meter element 3
Power Registers
| 1009, 1010 | PowerSum | PowerSum | W | Read-Only |  | Active power, sum of active phases
| 1011, 1012 | Power1 | PowerA | W | Read-Only |  | Active power, meter element 1
| 1013, 1014 | Power2 | PowerB | W | Read-Only |  | Active power, meter element 2
| 1015, 1016 | Power3 | PowerC | W | Read-Only |  | Active power, meter element 3
| 1035, 1036 | SecondsFast |  | seconds | Read-Only |  | Seconds for last 24 hours, updates at 10 hz. Rolls over at 86400.
| 1037, 1038 | PowerFastSum |  | W | Read-Only |  | Active power, sum of active phases, updates at 10 Hz. No averaging
| 1039, 1040 | PowerFast1 |  | W | Read-Only |  | Active power, meter element 1, updates at 10 Hz. No averaging
| 1041, 1042 | PowerFast2 |  | W | Read-Only |  | Active power, meter element 2, updates at 10 Hz. No averaging
| 1043, 1044 | PowerFast3 |  | W | Read-Only |  | Active power, meter element 3, updates at 10 Hz. No averaging
Reactive and Apparent Energy Registers
| 1123, 1124 | EnergyReacSum | EnergyReacSum | kVARh | Read/Write |  | Reactive energy, sum of active phases
| 1125, 1126 | EnergyReac1 | EnergyReacA | kVARh | Read/Write |  | Net reactive energy, meter element 1
| 1127, 1128 | EnergyReac2 | EnergyReacB | kVARh | Read/Write |  | Net reactive energy, meter element 2
| 1129, 1130 | EnergyReac3 | EnergyReacC | kVARh | Read/Write |  | Net reactive energy, meter element 3
| 1189, 1190 | EnergyReacPosSum |  | kVARh | Read/Write |  | Positive reactive energy, sum of active phases
| 1183, 1184 | EnergyReacPos1 |  | kVARh | Read/Write |  | Positive reactive energy, meter element 1
| 1185, 1186 | EnergyReacPos2 |  | kVARh | Read/Write |  | Positive reactive energy, meter element 2
| 1187, 1188 | EnergyReacPos3 |  | kVARh | Read/Write |  | Positive reactive energy, meter element 3
| 1197, 1198 | EnergyReacNegSum |  | kVARh | Read/Write |  | Negative reactive energy, sum of active phases
| 1191, 1192 | EnergyReacNeg1 |  | kVARh | Read/Write |  | Negative reactive energy, meter element 1
| 1193, 1194 | EnergyReacNeg2 |  | kVARh | Read/Write |  | Negative reactive energy, meter element 2
| 1195, 1196 | EnergyReacNeg3 |  | kVARh | Read/Write |  | Negative reactive energy, meter element 3
| 1131, 1132 | EnergyAppSum | EnergyAppSum | kVAh | Read/Write |  | Apparent energy, sum of active phases
| 1133, 1134 | EnergyApp1 | EnergyAppA | kVAh | Read/Write |  | Apparent energy, meter element 1
| 1135, 1136 | EnergyApp2 | EnergyAppB | kVAh | Read/Write |  | Apparent energy, meter element 2
| 1137, 1138 | EnergyApp3 | EnergyAppC | kVAh | Read/Write |  | Apparent energy, meter element 3
Reactive and Apparent Power Registers
| 1147, 1148 | PowerReacSum | PowerReacSum | VAR | Read-Only |  | Reactive power, sum of active phases
| 1149, 1150 | PowerReac1 | PowerReacA | VAR | Read-Only |  | Reactive power, meter element 1
| 1151, 1152 | PowerReac2 | PowerReacB | VAR | Read-Only |  | Reactive power, meter element 2
| 1153, 1154 | PowerReac3 | PowerReacC | VAR | Read-Only |  | Reactive power, meter element 3
| 1155, 1156 | PowerAppSum | PowerAppSum | VA | Read-Only |  | Apparent power, sum of active phases
| 1157, 1158 | PowerApp1 | PowerAppA | VA | Read-Only |  | Apparent power, meter element 1
| 1159, 1160 | PowerApp2 | PowerAppB | VA | Read-Only |  | Apparent power, meter element 2
| 1161, 1162 | PowerApp3 | PowerAppC | VA | Read-Only |  | Apparent power, meter element 3
Voltage Registers
| 1017, 1018 | VoltAvgLN | VoltAvgLN | V | Read-Only |  | Average phase-to-neutral voltage
| 1019, 1020 | VoltAN | VoltA | V | Read-Only |  | RMS voltage, phase A to neutral
| 1021, 1022 | VoltBN | VoltB | V | Read-Only |  | RMS voltage, phase B to neutral
| 1023, 1024 | VoltCN | VoltC | V | Read-Only |  | RMS voltage, phase C to neutral
| 1025, 1026 | VoltAvgLL | VoltAvgLL | V | Read-Only |  | Average line-to-line voltage
| 1027, 1028 | VoltAB | VoltAB | V | Read-Only |  | RMS voltage, line-to-line, phase A to B
| 1029, 1030 | VoltBC | VoltBC | V | Read-Only |  | RMS voltage, line-to-line, phase B to C
| 1031, 1032 | VoltCA | VoltAC | V | Read-Only |  | RMS voltage, line-to-line, phase A to C
Current Registers
| 1163, 1164 | Current1 | CurrentA | A | Read-Only |  | RMS current, meter element 1
| 1165, 1166 | Current2 | CurrentB | A | Read-Only |  | RMS current, meter element 2
| 1167, 1168 | Current3 | CurrentC | A | Read-Only |  | RMS current, meter element 3
Frequency Register
| 1033, 1034 | Freq | Freq | Hz | Read-Only |  | Power line frequency
Power Factor Registers
| 1139, 1140 | PowerFactorAvg | PowerFactorAvg |  | Read-Only |  | Apparent power factor, average of active phases
| 1141, 1142 | PowerFactor1 | PowerFactorA |  | Read-Only |  | Apparent power factor, meter element 1
| 1143, 1144 | PowerFactor2 | PowerFactorB |  | Read-Only |  | Apparent power factor, meter element 2
| 1145, 1146 | PowerFactor3 | PowerFactorC |  | Read-Only |  | Apparent power factor, meter element 3
Demand Registers
| 1169, 1170 | DemandSum | Demand | W | Read-Only |  | Active power demand averaged over the demand period
| 1171, 1172 | DemandSumMin | DemandMin | W | Read-Only |  | Minimum power demand
| 1173, 1174 | DemandSumMax | DemandMax | W | Read-Only |  | Maximum power demand
| 1175, 1176 | DemandAppSum | DemandApp | W | Read-Only |  | Apparent power demand
| 1177, 1178 | Demand1 | DemandA | W | Read-Only |  | Active power demand, meter element 1
| 1179, 1180 | Demand2 | DemandB | W | Read-Only |  | Active power demand, meter element 2
| 1181, 1182 | Demand3 | DemandC | W | Read-Only |  | Active power demand, meter element 3
Measurement Register List - Integer
| Registers | Name | WNC Name | Units | Access | Default | Description
Energy Registers
| 1201, 1202 | EnergySum | EnergySum | 0.1 kWh | Read/Write |  | Total net (bidirectional) energy
| 1205, 1206 | EnergySumNR | EnergySumNR | 0.1 kWh | Read-Only |  | Total net (bidirectional) energy - non resettable
| 1301, 1302 | Energy1 | EnergyA | 0.1 kWh | Read/Write |  | Net energy, meter element 1
| 1303, 1304 | Energy2 | EnerygB | 0.1 kWh | Read/Write |  | Net energy, meter element 2
| 1305, 1306 | Energy3 | EnergyC | 0.1 kWh | Read/Write |  | Net energy, meter element 3
| 1203, 1204 | EnergyPosSum | EnergyPosSum | 0.1 kWh | Read/Write |  | Total positive energy
| 1207, 1208 | EnergyPosSumNR | EnergyPosSumNR | 0.1 kWh | Read-Only |  | Total positive energy - non resettable
| 1307, 1308 | EnergyPos1 | EnergyPosA | 0.1 kWh | Read/Write |  | Positive energy, meter element 1
| 1309, 1310 | EnergyPos2 | EnergyPosB | 0.1 kWh | Read/Write |  | Positive energy, meter element 2
| 1311, 1312 | EnergyPos3 | EnergyPosC | 0.1 kWh | Read/Write |  | Positive energy, meter element 3
| 1313, 1314 | EnergyNegSum | EnergyNegSum | 0.1 kWh | Read/Write |  | Negative energy, sum of active phases
| 1315, 1316 | EnergyNegSumNR | EnergyNegSumNR | 0.1 kWh | Read-Only |  | Negative energy, sum of active phases - non resettable
| 1317, 1318 | EnergyNeg1 | EnergyNegA | 0.1 kWh | Read/Write |  | Negative energy, meter element 1
| 1319, 1320 | EnergyNeg2 | EnergyNegB | 0.1 kWh | Read/Write |  | Negative energy, meter element 2
| 1321, 1322 | EnergyNeg3 | EnergyNegC | 0.1 kWh | Read/Write |  | Negative energy, meter element 3
Power Registers
| 1209 | PowerSum | PowerSum | PowerIntScale | Read-Only |  | Active power, sum of active phases
| 1210 | Power1 | PowerA | PowerIntScale | Read-Only |  | Active power, meter element 1
| 1211 | Power2 | PowerB | PowerIntScale | Read-Only |  | Active power, meter element 2
| 1212 | Power3 | PowerC | PowerIntScale | Read-Only |  | Active power, meter element 3
Reactive Energy Registers
| 1323, 1324 | EnergyReacSum | EnergyReacSum | 0.1 kVARh | Read/Write |  | Reactive energy, sum of active phases
| 1325, 1326 | EnergyReac1 | EnergyReacA | 0.1 kVARh | Read/Write |  | Net reactive energy, meter element 1
| 1327, 1328 | EnergyReac2 | EnergyReacB | 0.1 kVARh | Read/Write |  | Net reactive energy, meter element 2
| 1329, 1330 | EnergyReac3 | EnergyReacC | 0.1 kVARh | Read/Write |  | Net reactive energy, meter element 3
| 1370, 1371 | EnergyReacPosSum |  | 0.1 kVARh | Read/Write |  | Positive reactive energy, sum of active phases
| 1364, 1365 | EnergyReacPos1 |  | 0.1 kVARh | Read/Write |  | Positive reactive energy, meter element 1
| 1366, 1367 | EnergyReacPos2 |  | 0.1 kVARh | Read/Write |  | Positive reactive energy, meter element 2
| 1368, 1369 | EnergyReacPos3 |  | 0.1 kVARh | Read/Write |  | Positive reactive energy, meter element 3
| 1378, 1379 | EnergyReacNegSum |  | 0.1 kVARh | Read/Write |  | Negative reactive energy, sum of active phases
| 1372, 1373 | EnergyReacNeg1 |  | 0.1 kVARh | Read/Write |  | Negative reactive energy, meter element 1
| 1374, 1375 | EnergyReacNeg2 |  | 0.1 kVARh | Read/Write |  | Negative reactive energy, meter element 2
| 1376, 1377 | EnergyReacNeg3 |  | 0.1 kVARh | Read/Write |  | Negative reactive energy, meter element 3
| 1331, 1332 | EnergyAppSum | EnergyAppSum | 0.1 kVAh | Read/Write |  | Apparent energy, sum of active phases
| 1333, 1334 | EnergyApp1 | EnergyAppA | 0.1 kVAh | Read/Write |  | Apparent energy, meter element 1
| 1335, 1336 | EnergyApp2 | EnergyAppB | 0.1 kVAh | Read/Write |  | Apparent energy, meter element 2
| 1337, 1338 | EnergyApp3 | EnergyAppC | 0.1 kVAh | Read/Write |  | Apparent energy, meter element 3
Reactive and Apparent Power Registers
| 1343 | PowerReacSum | PowerReacSum | PowerIntScale | Read-Only |  | Reactive power VAR, sum of active phases
| 1344 | PowerReac1 | PowerReacA | PowerIntScale | Read-Only |  | Reactive power VAR, meter element 1
| 1345 | PowerReac2 | PowerReacB | PowerIntScale | Read-Only |  | Reactive power VAR, meter element 2
| 1346 | PowerReac3 | PowerReacC | PowerIntScale | Read-Only |  | Reactive power VAR, meter element 3
| 1347 | PowerAppSum | PowerAppSum | PowerIntScale | Read-Only |  | Apparent power VA, sum of active phases
| 1348 | PowerApp1 | PowerAppA | PowerIntScale | Read-Only |  | Apparent power VA, meter element 1
| 1349 | PowerApp2 | PowerAppB | PowerIntScale | Read-Only |  | Apparent power VA, meter element 2
| 1350 | PowerApp3 | PowerAppC | PowerIntScale | Read-Only |  | Apparent power VA, meter element 3
Voltage Registers
| 1213 | VoltAvgLN | VoltAvgLN | 0.1 V | Read-Only |  | Average phase-to-neutral voltage
| 1214 | VoltAN | VoltA | 0.1 V | Read-Only |  | RMS voltage, phase A to neutral
| 1215 | VoltBN | VoltB | 0.1 V | Read-Only |  | RMS voltage, phase B to neutral
| 1216 | VoltCN | VoltC | 0.1 V | Read-Only |  | RMS voltage, phase C to neutral
| 1217 | VoltAvgLL | VoltAvgLL | 0.1 V | Read-Only |  | Average line-to-line voltage
| 1218 | VoltAB | VoltAB | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase A to B
| 1219 | VoltBC | VoltBC | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase B to C
| 1220 | VoltCA | VoltAC | 0.1 V | Read-Only |  | RMS voltage, line-to-line, phase A to C
Current Registers
| 1351 | Current1 | CurrentA | CurrentIntScale | Read-Only |  | RMS current, meter element 1
| 1352 | Current2 | CurrentB | CurrentIntScale | Read-Only |  | RMS current, meter element 2
| 1353 | Current3 | CurrentC | CurrentIntScale | Read-Only |  | RMS current, meter element 3
Frequency Register
| 1221 | Freq | Freq | 0.1 Hz | Read-Only |  | Power line frequency
Power Factor Registers
| 1339 | PowerFactorAvg | PowerFactorAvg | 0.01 | Read-Only |  | Apparent power factor, average of active phases
| 1340 | PowerFactor1 | PowerFactorA | 0.01 | Read-Only |  | Apparent power factor, meter element 1
| 1341 | PowerFactor2 | PowerFactorB | 0.01 | Read-Only |  | Apparent power factor, meter element 2
| 1342 | PowerFactor3 | PowerFactorC | 0.01 | Read-Only |  | Apparent power factor, meter element 3
Demand Registers
| 1354 | DemandSum | Demand | PowerIntScale | Read-Only |  | Active power demand averaged over the demand period
| 1355 | DemandSumMin | DemandMin | PowerIntScale | Read-Only |  | Minimum power demand
| 1356 | DemandSumMax | DemandMax | PowerIntScale | Read-Only |  | Maximum power demand
| 1357 | DemandAppSum | DemandApp | PowerIntScale | Read-Only |  | Apparent power demand
| 1358 | Demand1 | DemandA | PowerIntScale | Read-Only |  | Active power demand, meter element 1
| 1359 | Demand2 | DemandB | PowerIntScale | Read-Only |  | Active power demand, meter element 2
| 1360 | Demand3 | DemandC | PowerIntScale | Read-Only |  | Active power demand, meter element 3
Configuration Registers
| Registers | Name | WNC Name | Units | Access | Default | Description
| 1601, 1602 | ConfigPasscode | ConfigPasscode |  | Read/Write | 0 | Optional passcode to prevent unauthorized changes to configuration
| 1603 | CtAmps | CtAmps | 1 A | Read/Write | 5 | Current transformer rated current
| 1604 | CtAmps1 | CtAmpsA | 1 A | Read/Write | 5 | Optional CT rated current override for CT1
| 1605 | CtAmps2 | CtAmpsB | 1 A | Read/Write | 5 | Optional CT rated current override for CT2
| 1606 | CtAmps3 | CtAmpsC | 1 A | Read/Write | 5 | Optional CT rated current override for CT3
| 1607 | CtDirections | CtDirections |  | Read/Write | 0 | Optionally invert CT orientations
| 1608 | Averaging | Averaging |  | Read/Write | 1 = 5 sec | Configure measurement averaging
| 1609 | PowerIntScale | PowerIntScale | 1 W | Read/Write | 0 (auto) | Scale factor for integer power registers
| 1610 | DemPerMins | DemPerMins | 1 minute | Read/Write | 15 | Demand period
| 1611 | DemSubints | DemSubints |  | Read/Write | 1 | Number of demand subintervals
| 1612 | GainAdjust1 | GainAdjustA | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for CT1
| 1613 | GainAdjust2 | GainAdjustB | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for CT2
| 1614 | GainAdjust3 | GainAdjustC | 1/10000th | Read/Write | 10000 | Optional power/energy adjustment for CT3
| 1615 | PhaseAdjust1 | PhaseAdjustA | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for CT1
| 1616 | PhaseAdjust2 | PhaseAdjustB | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for CT2
| 1617 | PhaseAdjust3 | PhaseAdjustC | 0.001 deg | Read/Write | -1000 | Optional CT phase angle adjust for CT3
| 1618 | CreepLimit | CreepLimit |  | Read/Write | 400 | Configure minimum power for a non-zero reading
| 1619 | PhaseOffset | PhaseOffset | 1 degree | Read/Write | 120 | No longer used
| 1620 | ZeroEnergy | ZeroEnergy |  | Read/Write | - | Write 1 to zero all resettable energy registers
| 1621 | ZeroDemand | ZeroDemand |  | Read/Write | - | Write 1 to zero all demand values
| 1622 | CurrentIntScale | CurrentIntScale |  | Read/Write | 20000 | Scale factor for integer current registers
| 1623 | Deleted | IoPinMode |  | Read/Write | 0
| 1624 | MeterConfig1 |  |  | Read/Write | 10 | Line-to-line or line-to-neutral voltage paired with CT1. This is reported through Power1, Energy1, etc. 0 = Disable meter element 10 = Van, 20 = Vbn, 30 = Vcn 40 = Vab, 50 = Vbc, 60 = Vca 70 = Vba, 80 = Vcb, 90 = Vac
| 1625 | MeterConfig2 |  |  | Read/Write | 20 | Line-to-line or line-to-neutral voltage paired with CT2. This is reported through Power2, Energy2, etc.
| 1626 | MeterConfig3 |  |  | Read/Write | 30 | Line-to-line or line-to-neutral voltage paired with CT3. This is reported through Power3, Energy3, etc.
| 1627 | Reserved |  |  |  | 0
| 1628 | ChangeCounter |  | Uint16 | Read-Only |  | Reports the number of times the meter configuration has been changed
| 1629, 1630 | NominalCtVolts1 |  | Float32 volts | Read/Write | 0.33333 | CT1, Voltage of full scale CT signal
| 1631, 1632 | NominalCtVolts2 |  | Float32 volts | Read/Write | 0.33333 | CT2, Voltage of full scale CT signal
| 1633, 1634 | NominalCtVolts3 |  | Float32 volts | Read/Write | 0.33333 | CT3, Voltage of full scale CT signal
| 1636 | ConnectionType |  | Int16 | Read/Write | 1 | Shortcut to set all three MeterConfig registers at once. 0=Custom, 1=Wye, 2=Delta, 3=Branch circuits, 4=House and inverter, 5=Line to Line
| 1637 | VoltsNoiseFloor |  | Int16 | Read/Write | 200 | Configure minimum voltage for active phases
| 1638 | CtMonitoring |  | Int16 | Read/Write | 0 | Configure disconnected CT detection (0 to 2) 0 - Disable disconnected CT detection. 1 - Detect disconnected CTs. Force disconnected readings to zero. 2 - Detect disconnected CTs. Force disconnected readings to 32767 (integer) or Nan (floating-point).
| 1639 | PtRatio |  | Float32 | Read/Write | 1 | Potential transformer ratio (0.05 to 300.0)
| 1685 | OptSignedCurrent |  | Int16 | Read/Write | 0 | Option to report signed current. 0=unsigned current (default), 1=signed current where the sign matches the sign of the active power.
| 1686 | OptEnergySumMethod |  | Int16 | Read/Write | 0 | Option to specify the method by which energyPosSum and energyNegSum registers are accumulated.
Communication Registers
| Registers | Name | WNC Name | Units | Access | Default | Description
| 1651 | ApplyComConfig | ApplyComConfig |  | Read/Write | 0 | Writing 1234 applies the configuration settings below. Reads 1 if changes not applied yet.
| 1652 | Address | Address |  | Read/Write | 0 | Modbus address (if non-zero, overrides DIP switches)
| 1653 | BaudRate | BaudRate |  | Read/Write | 0 for models with DIP switch 5 otherwise | 0 = DIP Switch Assigned 1 = 1200, 2 = 2400, 3 = 4800, 4 = 9600, 5 = 19200, 6 = 38400 7 = 57600, 8 = 76800, 9 = 115200
| 1654 | ParityMode | ParityMode |  | Read/Write | 0 | 0 = N81 (no parity, one stop bit) 1 = E81 (even parity, one stop bit)
| 1655 | ModbusMode | ModbusMode |  | Read/Write | 0 | 0=RTU
| 1656 | ReplyDelay | ReplyDelay |  | Read/Write | 5 | Minimum Modbus reply delay. 5 to 180 ms
| 1657, 1658 | SerialNumberKey |  |  | Read/Write | - | Serial number of meter to change Modbus address
| 1659 | NewAddress |  |  | Read/Write | - | New Modbus address for meter with SerialNumberKey
Customer Diagnostic Registers - Integer
| Registers | Name | WNC Name | Units | Access | Default | Description
| 1, 2 | DummyReg | DummyReg |  | Read-Only |  | Dummy register; always returns zero; can be used to scan for active Modbus addresses
| 1701, 1702 | SerialNumber | SerialNumber |  | Read-Only |  | The unique WattNode serial number
| 1703, 1704 | UptimeSecs | UptimeSecs | Seconds | Read-Only |  | Time in seconds since last power on
| 1705, 1706 | TotalSecs | TotalSecs | Seconds | Read-Only |  | Total seconds of operation
| 1707 | Model | Model |  | Read-Only |  | Encoded WattNode model 510 = WND-WR-MB 530 = WND-M0-MB, WND-M1-MB
| 1708 | Version | Version |  | Read-Only |  | Firmware version
| 1710 | ErrorStatusQueue | ErrorStatus | n.a. | Read/Write |  | List of recent errors and events
| 1711 | PowerFailCount | PowerFailCount |  | Read/Write |  | Power failure count
| 1712 | CrcErrorCount | CrcErrorCount |  | Read/Write |  | Count of Modbus CRC communication errors
| 1713 | FrameErrorCount | FrameErrorCount |  | Read/Write |  | Count of Modbus framing errors
| 1714 | PacketErrorCount | PacketErrorCount |  | Read/Write |  | Count of bad Modbus packets
| 1715 | OverrunCount | OverrunCount |  | Read/Write |  | Count of Modbus buffer overruns
| 1716 | ErrorStatus1 | ErrorStatus1 | n.a. | Read/Write |  | Newest error or event (0 = no errors)
| 1717 | ErrorStatus2 | ErrorStatus2 | n.a. | Read/Write |  | Next oldest error or event
| 1718 | ErrorStatus3 | ErrorStatus3 | n.a. | Read/Write |  | Next oldest error or event
| 1719 | ErrorStatus4 | ErrorStatus4 | n.a. | Read/Write |  | Next oldest error or event
| 1720 | ErrorStatus5 | ErrorStatus5 | n.a. | Read/Write |  | Next oldest error or event
| 1721 | ErrorStatus6 | ErrorStatus6 | n.a. | Read/Write |  | Next oldest error or event
| 1722 | ErrorStatus7 | ErrorStatus7 | n.a. | Read/Write |  | Next oldest error or event
| 1723 | ErrorStatus8 | ErrorStatus8 | n.a. | Read/Write |  | Oldest error or event
| 1760 | CtStatus1 |  | n.a. | Read/Write |  | Status of CT1 disconnect detection: 0 = Normal or no monitoring 1 = CT disconnected 2 = CT reconnected (was disconnected)
| 1761 | CtStatus2 |  | n.a. | Read/Write |  | Status of CT2 disconnect detection
| 1762 | CtStatus3 |  | n.a. | Read/Write |  | Status of CT3 disconnect detection
Option Information Registers - Integer
| Registers | Name | WNC Name | Units | Access | Default | Description
| 1709 | Options | Options |  | Read-Only | 0 | WattNode options
| 1724 | OptCtAmps1 | OptCtAmps1 | 1 A | Read-Only | 0 | Factory programmed CtAmps1 value
| 1725 | OptCtAmps2 | OptCtAmps2 | 1 A | Read-Only | 0 | Factory programmed CtAmps2 value
| 1726 | OptCtAmps3 | OptCtAmps3 | 1 A | Read-Only | 0 | Factory programmed CtAmps3 value
| 1727 | Deleted | OptModbusMode |  | Read-Only | 0 | Always returns 0
| 1728 | OptAddress | OptAddress |  | Read-Only | 0 | Factory programmed Modbus slave address
| 1729 | OptBaudRate | OptBaudRate |  | Read-Only | 0 | Factory programmed Modbus baud rate (see BaudRate register)
| 1730 | OptParityMode | OptParityMode |  | Read-Only | 0 | Factory programmed Modbus parity mode (see ParityMode register)
| 1737 | OptLockedConfig | OptLockedConfig |  | Read-Only | 0 | Factory option for CtAmps and other configuration settings locked
| 1738 | Deleted | OptFastPower |  | Read-Only | 0 | Always returns 0
| 1739 | OptRs485Termination |  |  | Read-Only | 0 | DIP switch 7 controls RS-485 termination
| 1740 | OptOemFeatures |  |  | Read-Only | 0 | Factory option for OEM features
| 1741 | OptNrEnergies |  |  | Read-Only | 0 | Factory option for all energies non-resettable